## Info
Site | Example Site D
Date | 2026-08-31
Surveyed by | A. Ardigo
Notes | Config 4 - dual MV boards, riser feeders, N.O. tie

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
MV1 | MV Incomer | Utility incomer A |  | 11 kV
MV2 | MV Incomer | Utility incomer B |  | 11 kV
MVB1 | MV Busbar | MV switchboard A | 630 A | 11 kV | CB | MV1 | 6 feeders to risers
MVB2 | MV Busbar | MV switchboard B | 630 A | 11 kV | CB | MV2 | 6 feeders to risers
TIE1 | Bus Coupler | MV bus tie | 630 A | 11 kV | CB | MVB1, MVB2 | Normally open
TX1 | Transformer | Riser R1, Dyn11 | 1600 kVA | 11/0.4 kV | CB | MVB1
TX2 | Transformer | Riser R2, Dyn11 | 1250 kVA | 11/0.4 kV | CB | MVB1
TX3 | Transformer | Riser R3, Dyn11 | 1000 kVA | 11/0.4 kV | CB | MVB1
P1 | Pump | CHW pump 1 | 315 kW | 11 kV | Fuse-contactor | MVB1
P2 | Pump | CHW pump 2 | 315 kW | 11 kV | Fuse-contactor | MVB1
P3 | Pump | CW pump 1 | 160 kW | 11 kV | Fuse-contactor | MVB1
LVB1 | LV Busbar | LV board R1 | 2500 A | 400 V | CB | TX1
MCC1 | MCC | AHU plant | 400 A | 400 V | CB | LVB1
MCC2 | MCC | Pump room | 400 A | 400 V | CB | LVB1
MCC3 | MCC | Ventilation | 250 A | 400 V | CB | LVB1
LVB2 | LV Busbar | LV board R2 | 2000 A | 400 V | CB | TX2
MCC4 | MCC | AHU plant | 400 A | 400 V | CB | LVB2
MCC5 | MCC | Ventilation | 250 A | 400 V | CB | LVB2
LVB3 | LV Busbar | LV board R3 | 1600 A | 400 V | CB | TX3
MCC6 | MCC | AHU plant | 400 A | 400 V | CB | LVB3
MCC7 | MCC | Ventilation | 250 A | 400 V | CB | LVB3
TX4 | Transformer | Riser R4, Dyn11 | 1600 kVA | 11/0.4 kV | CB | MVB2
TX5 | Transformer | Riser R5, Dyn11 | 1250 kVA | 11/0.4 kV | CB | MVB2
TX6 | Transformer | Riser R6, Dyn11 | 1000 kVA | 11/0.4 kV | CB | MVB2
P4 | Pump | CHW pump 3 | 315 kW | 11 kV | Fuse-contactor | MVB2
P5 | Pump | CHW pump 4 | 315 kW | 11 kV | Fuse-contactor | MVB2
P6 | Pump | CW pump 2 | 160 kW | 11 kV | Fuse-contactor | MVB2
LVB4 | LV Busbar | LV board R4 | 2500 A | 400 V | CB | TX4
MCC8 | MCC | AHU plant | 400 A | 400 V | CB | LVB4
MCC9 | MCC | Pump room | 400 A | 400 V | CB | LVB4
MCC10 | MCC | Ventilation | 250 A | 400 V | CB | LVB4
LVB5 | LV Busbar | LV board R5 | 2000 A | 400 V | CB | TX5
MCC11 | MCC | AHU plant | 400 A | 400 V | CB | LVB5
MCC12 | MCC | Ventilation | 250 A | 400 V | CB | LVB5
LVB6 | LV Busbar | LV board R6 | 1600 A | 400 V | CB | TX6
MCC13 | MCC | AHU plant | 400 A | 400 V | CB | LVB6
MCC14 | MCC | Ventilation | 250 A | 400 V | CB | LVB6

## How to fill
HOW TO FILL THIS WORKBOOK (on site)
Yellow cells are the ones to fill in. Everything else is fixed.
1. Info sheet: site name, date, surveyor, free notes.
2. Equipment sheet: one row per item, top of the network first.
- ID: short unique tag you invent (MV1, RMU1, TX1, BB1, F1...).
- Type: pick from the dropdown (MV Incomer, Generator, MV
Busbar, RMU, Transformer, Pump, LV Busbar, Feeder, MCC,
Bus Coupler, Capacitor Bank, Earthing/NER, Surge Arrester).
One Transformer type covers step-down and step-up: which
way it is drawn follows Feeds From. A transformer that
feeds an MV board is a step-up, drawn above it with its
source on top; one hung under an MV board whose load is a
Generator is the same step-up drawn upside down. Write
'step-up' in Description - the voltages say it too.
MV Busbar = an MV switchboard; Pump = an MV motor load;
MCC = motor control centre on an LV board. A Bus Coupler
between two MV Busbars is the bus tie; one between a board
and a Generator is a changeover (ATS). A Generator can also
feed a board directly: name it in the board's Feeds From.
An LV Busbar fed from a Feeder or another LV Busbar is a
sub-board, drawn on the row below. A Feeder on MV gear is
an outgoing cable way. Capacitor Bank, Earthing/NER and
Surge Arrester need no load; a Feeder whose words say
capacitor / NER / arrester is drawn as one anyway.
Notes: 'VSD' on a motor draws a drive box, 'Spare' dashes
the way, 'N.O.' on an RMU marks the ring's open point.
- Rating / Voltage: as read from the nameplate (e.g. 1000 kVA,
11/0.4 kV, 630 A, 400 V).
- Protection: the device on THIS item's supply side - pick
CB, LBS, Fuse, Fuse-switch, Contactor or Fuse-contactor (an
MV motor starter = fuse + contactor), or leave blank for
the usual default. Two supplies: comma list in the same
order as Feeds From (e.g. LBS, CB). Free text on a busbar
(e.g. 87B differential) is printed next to its label.
- Feeds From: the ID of the item supplying this one. Use a comma
for two supplies (bus coupler between BB1, BB2 - or an RMU fed
by ring incomers MV1, MV2).
3. Back at the office: python sld_sketch.py thisfile.xlsx
and you get the single-line diagram as an SVG.