## Info
Site | L2 sections and ties
Notes | multi-level test

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
U1 | MV Incomer | Utility A |  | 33 kV
U2 | MV Incomer | Utility B |  | 33 kV
HVA | MV Busbar | 33 kV sec A | 630 A | 33 kV | CB | U1
HVB | MV Busbar | 33 kV sec B | 630 A | 33 kV | CB | U2
HVT | Bus Coupler | 33 kV tie |  | 33 kV | CB | HVA, HVB | Normally open
GTA | Transformer | Grid tx A | 10 MVA | 33/11 kV | CB | HVA
GTB | Transformer | Grid tx B | 10 MVA | 33/11 kV | CB | HVB
MVA | MV Busbar | 11 kV sec A | 1250 A | 11 kV | CB | GTA
MVB | MV Busbar | 11 kV sec B | 1250 A | 11 kV | CB | GTB
MVT | Bus Coupler | 11 kV tie |  | 11 kV | CB | MVA, MVB | Normally open
TA | Transformer | Dist tx A | 1600 kVA | 11/0.4 kV | CB | MVA
TB | Transformer | Dist tx B | 1600 kVA | 11/0.4 kV | CB | MVB
LVA | LV Busbar | LV sec A | 2500 A | 400 V | CB | TA
LVB | LV Busbar | LV sec B | 2500 A | 400 V | CB | TB
LVT | Bus Coupler | LV tie |  | 400 V | CB | LVA, LVB | Normally open
FA | Feeder | Feeder A | 250 A | 400 V | CB | LVA
FB | Feeder | Feeder B | 250 A | 400 V | CB | LVB