## Info
Site | C1 Water treatment works
Notes | 33/11/3.3/0.4 kV, dual utility, ring, gen

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
U1 | MV Incomer | Utility 33 kV A |  | 33 kV
U2 | MV Incomer | Utility 33 kV B |  | 33 kV
HV1 | MV Busbar | 33 kV board sec A | 1250 A | 33 kV | CB | U1
HV2 | MV Busbar | 33 kV board sec B | 1250 A | 33 kV | CB | U2
HVT | Bus Coupler | 33 kV bus section |  | 33 kV | CB | HV1, HV2 | Normally open
GT1 | Transformer | Grid tx A | 10 MVA | 33/11 kV | CB | HV1
GT2 | Transformer | Grid tx B | 10 MVA | 33/11 kV | CB | HV2
MV1 | MV Busbar | 11 kV board sec A | 1250 A | 11 kV | CB | GT1
MV2 | MV Busbar | 11 kV board sec B | 1250 A | 11 kV | CB | GT2
MVT | Bus Coupler | 11 kV bus section |  | 11 kV | CB | MV1, MV2 | Normally open
RMU1 | RMU | Sub 1 (intake) | 630 A | 11 kV | LBS | MV1
RMU2 | RMU | Sub 2 (filters) | 630 A | 11 kV | LBS, LBS | RMU1, RMU3
RMU3 | RMU | Sub 3 (chem) | 630 A | 11 kV | LBS | MV2 | N.O. point RMU2-RMU3
T1 | Transformer | Sub 1 tx | 1600 kVA | 11/0.4 kV | Fuse-switch | RMU1
T2 | Transformer | Sub 2 tx | 1600 kVA | 11/0.4 kV | Fuse-switch | RMU2
T3 | Transformer | Sub 3 tx | 1000 kVA | 11/0.4 kV | Fuse-switch | RMU3
PT | Transformer | Pump tx | 4 MVA | 11/3.3 kV | CB | MV1
PB | MV Busbar | 3.3 kV pump board | 1250 A | 3.3 kV | CB | PT
P1 | Pump | HL pump 1 | 800 kW | 3.3 kV | Fuse-contactor | PB
P2 | Pump | HL pump 2 | 800 kW | 3.3 kV | Fuse-contactor | PB
P3 | Pump | HL pump 3 (VSD) | 800 kW | 3.3 kV | CB | PB | via VSD
MSB1 | LV Busbar | Sub 1 MSB | 2500 A | 400 V | CB | T1
MSB2 | LV Busbar | Sub 2 MSB | 2500 A | 400 V | CB | T2
MSB3 | LV Busbar | Sub 3 MSB | 1600 A | 400 V | CB | T3
LT12 | Bus Coupler | MSB1-MSB2 tie |  | 400 V | CB | MSB1, MSB2 | Normally open
G1 | Generator | Standby genset | 1250 kVA | 400 V | CB |  | feeds MSB3 via ATS
ATS | Bus Coupler | ATS mains/gen |  | 400 V | CB | MSB3, G1 | changeover
M1 | MCC | Intake MCC |  | 400 V | CB | MSB1
M2 | MCC | Filter MCC |  | 400 V | CB | MSB2
M3 | MCC | Chem dosing MCC |  | 400 V | CB | MSB3
F1 | Feeder | Site lighting | 250 A | 400 V | CB | MSB1
F2 | Feeder | Admin building | 400 A | 400 V | CB | MSB2
F3 | Feeder | Workshop | 160 A | 400 V | CB | MSB3