## Info
Site | C2 Industrial building
Notes | LV cascade 3 deep, UPS, PFC, 690 V drives

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
INC | MV Incomer | Utility 11 kV |  | 11 kV
RMU | RMU | Intake RMU | 630 A | 11 kV | LBS | INC
TA | Transformer | Tx A | 2000 kVA | 11/0.4 kV | Fuse-switch | RMU
TB | Transformer | Tx B | 2000 kVA | 11/0.4 kV | Fuse-switch | RMU
MSBA | LV Busbar | MSB section A | 3200 A | 400 V | CB | TA
MSBB | LV Busbar | MSB section B | 3200 A | 400 V | CB | TB
TIE | Bus Coupler | MSB tie |  | 400 V | CB | MSBA, MSBB | Normally open
PFC | Feeder | PFC capacitor bank | 400 kvar | 400 V | CB | MSBA | capacitor bank
G1 | Generator | Standby genset | 1000 kVA | 400 V | CB |  | onto MSB-B via changeover
CO | Bus Coupler | Gen changeover |  | 400 V | CB | MSBB, G1
F1 | Feeder | DB-L1 feeder | 400 A | 400 V | MCCB | MSBA
DBL1 | LV Busbar | DB level 1 | 400 A | 400 V | MCCB | F1
F11 | Feeder | Lighting L1 | 63 A | 400 V | MCB | DBL1
F12 | Feeder | Small power L1 | 100 A | 400 V | MCB | DBL1
F13 | Feeder | DB-L1-East feeder | 160 A | 400 V | MCCB | DBL1
DBE | LV Busbar | DB L1 East | 160 A | 400 V | MCCB | F13
F131 | Feeder | Lights east | 32 A | 400 V | MCB | DBE
F132 | Feeder | Sockets east | 32 A | 400 V | RCBO | DBE
DBL2 | LV Busbar | DB level 2 | 400 A | 400 V | MCCB | MSBB
F21 | Feeder | Lighting L2 | 63 A | 400 V | MCB | DBL2
F22 | Feeder | HVAC L2 | 160 A | 400 V | MCCB | DBL2
UPS | Transformer | UPS 200 kVA | 200 kVA | 400/400 V | CB | MSBB | UPS - drawn as tx
DBC | LV Busbar | Critical DB (UPS) | 300 A | 400 V | MCCB | UPS
FC1 | Feeder | Server room | 125 A | 400 V | MCB | DBC
FC2 | Feeder | Control room | 63 A | 400 V | MCB | DBC
TD | Transformer | Drives tx | 800 kVA | 0.4/0.69 kV | CB | MSBA
DBD | LV Busbar | 690 V drives board | 1000 A | 690 V | CB | TD
MCD | MCC | Drives MCC |  | 690 V | CB | DBD
PD1 | Pump | Process pump 1 | 250 kW | 690 V | CB | DBD | VSD
MC1 | MCC | Process MCC A |  | 400 V | CB | MSBA
MC2 | MCC | Process MCC B |  | 400 V | CB | MSBB