## Info
Site | C3 Pumping station
Notes | MV motors, VSD, cap bank, NER

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
I1 | MV Incomer | Utility feeder 1 |  | 11 kV
I2 | MV Incomer | Utility feeder 2 |  | 11 kV
B1 | MV Busbar | 11 kV sec 1 | 2000 A | 11 kV | CB | I1
B2 | MV Busbar | 11 kV sec 2 | 2000 A | 11 kV | CB | I2
BT | Bus Coupler | Bus section |  | 11 kV | CB | B1, B2 | Normally open
P1 | Pump | Main pump 1 | 1.5 MW | 11 kV | CB | B1
P2 | Pump | Main pump 2 | 1.5 MW | 11 kV | CB | B1
P3 | Pump | Main pump 3 | 1.5 MW | 11 kV | CB | B2
VT4 | Transformer | VSD tx pump 4 | 2 MVA | 11/0.69 kV | CB | B1 | 12-pulse
P4 | Pump | Main pump 4 (VSD) | 1.5 MW | 690 V | Contactor | VT4
VT5 | Transformer | VSD tx pump 5 | 2 MVA | 11/0.69 kV | CB | B2 | 12-pulse
P5 | Pump | Main pump 5 (VSD) | 1.5 MW | 690 V | Contactor | VT5
P6 | Pump | Main pump 6 | 1.5 MW | 11 kV | CB | B2
CAP | Feeder | MV capacitor bank | 2 Mvar | 11 kV | CB | B1 | capacitor bank
ET | Transformer | Earthing tx + NER |  | 11 kV | CB | B1 | zig-zag, NER 400 A
ST1 | Transformer | Station tx 1 | 1000 kVA | 11/0.4 kV | CB | B1
ST2 | Transformer | Station tx 2 | 1000 kVA | 11/0.4 kV | CB | B2
LV1 | LV Busbar | Station LV sec 1 | 1600 A | 400 V | CB | ST1
LV2 | LV Busbar | Station LV sec 2 | 1600 A | 400 V | CB | ST2
LT | Bus Coupler | LV bus section |  | 400 V | CB | LV1, LV2 | Normally open
AUX | Transformer | Aux tx (lighting) | 100 kVA | 400/230 V | CB | LV1
DBA | LV Busbar | Lighting DB | 200 A | 230 V | CB | AUX
FA1 | Feeder | Lighting | 63 A | 230 V | MCB | DBA
MCC1 | MCC | Aux MCC 1 |  | 400 V | CB | LV1
MCC2 | MCC | Aux MCC 2 |  | 400 V | CB | LV2
F1 | Feeder | Cranes | 250 A | 400 V | CB | LV1
F2 | Feeder | Screens | 160 A | 400 V | CB | LV2
BC | Feeder | Battery charger 110 V DC |  | 400 V | CB | LV2 | DC system