## Info
Site | C4 Distribution ring
Notes | 5-RMU ring, N.O. at RMU3, sub-ring, LV cross-tie

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
INC | MV Incomer | Primary substation |  | 11 kV
PB | MV Busbar | Primary 11 kV board | 1250 A | 11 kV | CB | INC
R1 | RMU | RMU 1 | 630 A | 11 kV | CB, LBS | PB, R2
R2 | RMU | RMU 2 | 630 A | 11 kV | LBS, LBS | R1, R3
R3 | RMU | RMU 3 (N.O.) | 630 A | 11 kV | LBS, LBS | R2, R4 | ring open here
R4 | RMU | RMU 4 | 630 A | 11 kV | LBS, LBS | R3, R5
R5 | RMU | RMU 5 | 630 A | 11 kV | LBS, CB | R4, PB
R41 | RMU | RMU 4a (sub-ring) | 400 A | 11 kV | LBS, LBS | R4, R42
R42 | RMU | RMU 4b (sub-ring) | 400 A | 11 kV | LBS, LBS | R41, R4
T1 | Transformer | Tx 1 | 800 kVA | 11/0.4 kV | Fuse-switch | R1
T2 | Transformer | Tx 2 | 800 kVA | 11/0.4 kV | Fuse-switch | R2
T3 | Transformer | Tx 3 | 500 kVA | 11/0.4 kV | Fuse-switch | R3
T4 | Transformer | Tx 4 | 1000 kVA | 11/0.4 kV | Fuse-switch | R4
T5 | Transformer | Tx 5 | 800 kVA | 11/0.4 kV | Fuse-switch | R5
T41 | Transformer | Tx 4a | 315 kVA | 11/0.4 kV | Fuse-switch | R41
T42 | Transformer | Tx 4b | 315 kVA | 11/0.4 kV | Fuse-switch | R42
L1 | LV Busbar | LV 1 | 1250 A | 400 V | CB | T1
L2 | LV Busbar | LV 2 | 1250 A | 400 V | CB | T2
L3 | LV Busbar | LV 3 | 800 A | 400 V | CB | T3
L4 | LV Busbar | LV 4 | 1600 A | 400 V | CB | T4
L5 | LV Busbar | LV 5 | 1250 A | 400 V | CB | T5
L41 | LV Busbar | LV 4a | 500 A | 400 V | CB | T41
L42 | LV Busbar | LV 4b | 500 A | 400 V | CB | T42
XT | Bus Coupler | LV1-LV2 cross-tie |  | 400 V | CB | L1, L2 | Normally open, 300 m cable
F1 | Feeder | Feeder | 250 A | 400 V | CB | L1
F2 | Feeder | Feeder | 250 A | 400 V | CB | L2
F3 | Feeder | Feeder | 160 A | 400 V | CB | L3
F4 | Feeder | Feeder | 400 A | 400 V | CB | L4
F5 | Feeder | Feeder | 250 A | 400 V | CB | L5
F41 | Feeder | Feeder | 100 A | 400 V | CB | L41
F42 | Feeder | Feeder | 100 A | 400 V | CB | L42