## Info
Site | C5 Hybrid PV / BESS / gensets
Notes | multi-source, several step-ups

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
U | MV Incomer | Utility 33 kV |  | 33 kV
HV | MV Busbar | 33 kV POC board | 630 A | 33 kV | CB | U
GT | Transformer | Grid tx | 20 MVA | 33/11 kV | CB | HV
MV | MV Busbar | 11 kV main board | 2000 A | 11 kV | CB | GT
GB | MV Busbar | 11 kV generation board | 1250 A | 11 kV | CB, CB, CB, CB, CB, CB | MV, SU1, SU2, SU3, DG1, DG2 | islanding tie
PV1 | Generator | PV inverters block 1 | 2.5 MW | 400 V |  |  | inverter
PV2 | Generator | PV inverters block 2 | 2.5 MW | 400 V |  |  | inverter
PVB1 | LV Busbar | PV AC board 1 | 4000 A | 400 V | CB | PV1
PVB2 | LV Busbar | PV AC board 2 | 4000 A | 400 V | CB | PV2
SU1 | Transformer | PV step-up 1 | 3 MVA | 0.4/11 kV | CB | PVB1
SU2 | Transformer | PV step-up 2 | 3 MVA | 0.4/11 kV | CB | PVB2
BESS | Generator | BESS 2 MW / 4 MWh | 2 MW | 400 V |  |  | battery + PCS
BB | LV Busbar | BESS AC board | 3200 A | 400 V | CB | BESS
SU3 | Transformer | BESS step-up | 2.5 MVA | 0.4/11 kV | CB | BB
DG1 | Generator | Diesel genset 1 | 2 MVA | 11 kV | CB |  | MV genset
DG2 | Generator | Diesel genset 2 | 2 MVA | 11 kV | CB |  | MV genset
AT | Transformer | Aux tx | 500 kVA | 11/0.4 kV | CB | MV
AUX | LV Busbar | Aux LV board | 800 A | 400 V | CB | AT
FA1 | Feeder | Site services | 250 A | 400 V | CB | AUX
FA2 | Feeder | Control building | 160 A | 400 V | CB | AUX
SCADA | Transformer | UPS | 30 kVA | 400/400 V | CB | AUX | UPS
SDB | LV Busbar | SCADA DB | 63 A | 400 V | MCB | SCADA