## Info
Site | Example Site G
Date | 2026-09-02
Surveyed by | A. Ardigo
Notes | Config 7 - pump station, MCCs feed the motors

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
MV1 | MV Incomer | Utility supply |  | 11 kV
RMU1 | RMU | 3-way ring main unit | 630 A | 11 kV | LBS | MV1
TX1 | Transformer | Oil-immersed, Dyn11 | 1000 kVA | 11/0.4 kV | Fuse-switch | RMU1
MSB | LV Busbar | Main LV board | 1600 A | 400 V | CB | TX1
MCC1 | MCC | Pump MCC | 630 A | 400 V | CB | MSB
P1 | Pump | Raw water pump 1 | 55 kW | 400 V |  | MCC1 | Duty
P2 | Pump | Raw water pump 2 | 55 kW | 400 V |  | MCC1 | Standby
P3 | Pump | Booster pump | 30 kW | 400 V |  | MCC1 | VSD
P4 | Pump | Sump pump | 5.5 kW | 400 V | Fused contactor | MCC1
F5 | Feeder | MCC auxiliaries | 32 A | 400 V | MCB | MCC1
MCC2 | MCC | Blower MCC | 250 A | 400 V | CB | MSB
B1 | Pump | Blower 1 | 22 kW | 400 V |  | MCC2 | VSD
B2 | Pump | Blower 2 | 22 kW | 400 V |  | MCC2 | VSD
MCC3 | MCC | Dosing MCC | 100 A | 400 V | CB | MSB | Small motors, not surveyed
F1 | Feeder | Lighting and small power | 100 A | 400 V | CB | MSB
F2 | Feeder | Spare | 250 A | 400 V | CB | MSB | Spare

## How to fill
HOW TO FILL THIS WORKBOOK (on site)
Yellow cells are the ones to fill in. Everything else is fixed.
One row per item, top of the network first. The drawing's topology
comes only from ID and Feeds From: an item is drawn under whatever it
feeds from. Row order sets left-to-right order. A half-filled row still
draws, with an open terminal where the supply or the load is missing.
COLUMNS
ID a short unique tag you invent: MV1, RMU1, TX1, BB1, F1
Type pick from the dropdown (see TYPES)
Description free text, printed as a label (a few words also change
the symbol - see WORDS)
Rating from the nameplate: 1000 kVA, 630 A, 315 kW
Voltage from the nameplate: 11/0.4 kV, 400 V - printed only
Protection the device on THIS item's supply side: CB, LBS, Fuse,
Fuse-switch, Contactor, Fuse-contactor; blank = the usual
default; two supplies: a comma list in Feeds From order
(LBS, CB). Free text on a busbar (87B differential) is
printed as a zone label.
Feeds From the ID of the item supplying this one; comma for two
supplies (BB1, BB2 - MV1, MV2)
Notes anything worth remembering; printed on ties; a few
leading words change the symbol - see WORDS
TYPES (and how each one draws)
MV Incomer source tick at the top; feeds an MV Busbar, RMU or TX
MV Busbar thick bar, a breaker on every way; a board fed from
another board sits one tier lower
RMU dashed enclosure, load-break switches on the ways in,
fuse-switches on the tee-offs; RMUs that feed from
each other form a ring side by side
Transformer two circles; step-down or step-up follows Feeds From
Generator G circle over the board it feeds, on top of a step-up
column, or under a reversed one
Pump M 3~ circle: transformer row on MV gear, feeder band
on an LV board or an MCC, under a transformer of its own
LV Busbar thick bar with its feeders; fed from a Feeder or
another LV Busbar it is a sub-board on the row below
Feeder drop + device + arrow; on MV gear an outgoing cable
MCC labelled box; with Pumps/Feeders under it, a bus of
its own on the row below with the motor ways off it,
incomer, box and bus inside a dashed outline
Bus Coupler breaker between two busbars of the same kind; between
a board and a Generator, a changeover (ATS)
Capacitor Bank plates to earth (LV board or MV gear); needs no load
Earthing/NER resistor box to earth; needs no load
Surge Arrester arrester box to earth; needs no load
WIRING RECIPES (Feeds From)
Step-down: TX feeds from the MV board/RMU; the LV Busbar from TX.
Step-up from a genset or PV board: TX feeds from the Generator (or
generation LV Busbar); the MV Busbar/RMU feeds from TX.
Step-up from a live LV board: TX feeds from that board; the MV
gear feeds from TX.
Genset straight onto a board: the board feeds from MV, DG1, DG2;
the Generator rows have Feeds From blank.
Standby set on a changeover: a Bus Coupler row ATS feeding from
MSB3, G1.
Sub-board (DB): the LV Busbar feeds from the Feeder that supplies
it, or straight from the main LV Busbar.
Motors in an MCC: the MCC feeds from the board; each Pump from the MCC.
Bus tie: a Bus Coupler feeding from BB1, BB2; Notes Normally open.
Board with two supplies: the board feeds from TX1, TX2.
Ring of RMUs from a board: each RMU feeds from its neighbours
(PB, R2 ... R4, PB); a link written on both rows is drawn once.
Open point of a ring: Notes on one RMU: N.O. towards RMU2.
Spur or sub-ring off an RMU: the spur RMU feeds from the ring RMU;
a sub-ring's two RMUs feed from it and from each other.
Several voltage levels: the lower board feeds from the transformer,
the transformer from the upper board; tiers follow the wiring,
never the Voltage column.
Outgoing MV cable, capacitor bank, NER: a Feeder, Capacitor Bank
or Earthing/NER row feeding from the MV board or RMU.
WORDS THAT CHANGE THE SYMBOL (read from Description and Notes)
VSD / VFD / drive on a Pump: a drive box on the motor's drop
Spare / Future / at the start of Notes: the way drawn dashed
Out of service
N.O. / Normally open on a Bus Coupler: printed under it
N.O. towards RMU2, on an RMU: an N.O. marker on the cable to
ring open here the RMU named, or under the box
capacitor / PFC / kvar on a Feeder: drawn as a capacitor bank
NER / earthing / zig-zag on a Feeder, or a Transformer with nothing
on its output: earthing resistor / tx
arrester / surge on a Feeder: drawn as a surge arrester
Protection words: CB MCCB MCB ACB - LBS isolator - Fuse -
Fuse-switch SFU - Contactor - Fuse-contactor starter
BACK AT THE OFFICE
python sld_sketch.py thisfile.xlsx -> the SVG
python sld_sketch.py thisfile.xlsx --dxf -> SVG + DXF with the
equipment table
python sld_check.py thisfile.xlsx -> checks the drawing
against the table