## Info
Site | Tester2 W3 - Pump station
Date | 2026-09-02
Surveyed by | Tester 2
Notes | dedicated tx->MCC, MSB with MCCs, board tx, LV/LV tx

## Equipment
ID | Type | Description | Rating | Voltage | Protection | Feeds From | Notes
INC | MV Incomer | Utility 11 kV |  | 11 kV
RMU | RMU | 4-way RMU | 630 A | 11 kV | LBS | INC
TXA | Transformer | Pump MCC tx, Dyn11 | 1250 kVA | 11/0.4 kV | Fuse-switch | RMU | dedicated to MCC
MCCA | MCC | Main pump MCC | 2000 A | 400 V | CB | TXA
P1 | Pump | Sewage pump 1 | 160 kW | 400 V |  | MCCA | VSD
P2 | Pump | Sewage pump 2 | 160 kW | 400 V |  | MCCA | VSD
P3 | Pump | Sewage pump 3 | 160 kW | 400 V |  | MCCA
P4 | Pump | Sewage pump 4 | 160 kW | 400 V |  | MCCA | Spare
P5 | Pump | Storm pump 1 | 75 kW | 400 V | Fused contactor | MCCA
P6 | Pump | Storm pump 2 | 75 kW | 400 V | Fused contactor | MCCA
FA | Feeder | MCC auxiliaries | 63 A | 400 V | MCB | MCCA
TXB | Transformer | Station tx, Dyn11 | 800 kVA | 11/0.4 kV | Fuse-switch | RMU
MSB | LV Busbar | Station MSB | 1250 A | 400 V | CB | TXB
MCCP | MCC | Pump MCC (wash water) | 400 A | 400 V | CB | MSB
P7 | Pump | Wash water pump 1 | 30 kW | 400 V |  | MCCP
P8 | Pump | Wash water pump 2 | 30 kW | 400 V |  | MCCP | VSD
MCCB | MCC | Blower MCC | 630 A | 400 V | CB | MSB
B1 | Pump | Aeration blower 1 | 110 kW | 400 V |  | MCCB | VSD
B2 | Pump | Aeration blower 2 | 110 kW | 400 V |  | MCCB | VSD
B3 | Pump | Aeration blower 3 | 110 kW | 400 V |  | MCCB | Spare
TXM | Transformer | Screen motor supply | 75 kVA | 0.4/0.3 kV | CB | MSB
PM | Pump | Inlet screen motor | 37 kW | 300 V |  | TXM
TXL | Transformer | Lighting tx | 100 kVA | 0.4/0.23 kV | CB | MSB
SB230 | LV Busbar | 230 V lighting board | 250 A | 230 V | CB | TXL
FL1 | Feeder | Station lighting | 63 A | 230 V | MCB | SB230
FL2 | Feeder | Sockets and heaters | 63 A | 230 V | MCB | SB230
FL3 | Feeder | Spare | 32 A | 230 V | MCB | SB230 | Spare
F1 | Feeder | Control room UPS | 63 A | 400 V | MCCB | MSB
F2 | Feeder | Odour control unit | 160 A | 400 V | MCCB | MSB